## Busbars
Level 1 | SLD Reference | AutoSLDRef_13
New SLD Reference
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Type | Insulated
| Year of manufacturing | 0
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.00158
| MTTR, hrs | 0
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | IEEE Gold Book, 2007, Table 10.4, pg 252
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Cable Circuits
Level 1 | SLD Reference | AutoSLDRef_11
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Length, km | 0
| Cable circuit technology | Oil filled
| Type | Directly buried
| Year of manufacturing | 0
Additional Info | Sealing end technology | SF₆ to air
| Application | Capacitor Reactor
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.0876
| MTTR, hrs | 7.6
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | IEEE Gold Book, 2007, Table 10.4, pg 230
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Overhead Lines
Level 1 | SLD Reference | AutoSLDRef_12
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | HV
Level 2 | Length, km | 0
| Type | Wood
| Technology | Single pole (wood)
| Year of manufacturing | 0
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Circuit Breakers
Level 1 | SLD Reference | AutoSLDRef_1 | AutoSLDRef_5 | AutoSLDRef_6 | AutoSLDRef_7
New SLD Reference
| Bay ID | Default bay | Default bay | Default bay | Default bay
| Component technology | AIS | AIS | AIS | AIS
| Operating voltage, kV | 56 | 0 | 0 | 0
| Voltage type | HV | MV | MV | MV
Level 2 | Type | AIS Live Tank Breaker | AIS Live Tank Breaker | AIS Live Tank Breaker | AIS Dead Tank Breaker
| Year of manufacturing | 0 | 0 | 0 | 1999
Additional Info | Operation type | Single pole | Single pole | Single pole | Single pole
| Application | Bus | Bus | Bus | Bus
Manufacturer
Model
Serial number
| Comments |  |  |  | Test comments
Reliability Data | Library values
| Failure rate, times/yr | 0.001572 | 0 | 0 | 0
| MTTR, hrs | 6.5 | 0 | 0 | 0
| MTTS, hrs | 2.0415 | 0 | 0 | 0
| Maintenance frequency, times/yr | 0.0667 | 0 | 0 | 0
| MTTM, hrs | 4 | 0 | 0 | 0
| Source | Final Report of the 2004-2007 International Enquiry on Reliability of High Voltage Equipment, Part 2 - Reliability of High Voltage SF6 Circuit Breakers, WG A3.06, October 2012 - Table 2-21 base, Table 2-117 age
User defined values
Failure rate, times/yr
| MTTR, hrs |  |  | 1
| MTTS, hrs |  |  | 4
| Maintenance frequency, times/yr |  |  | 3
MTTM, hrs
Source
Other | Capital cost, USD | 0 | 0 | 0 | 0
| O&M cost, USD/yr | 0 | 0 | 0 | 0

## Disconnect Circuit Breakers
Level 1 | SLD Reference | AutoSLDRef_3
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | HV
Level 2 | Year of manufacturing | 0
Additional Info | Operation type | Single pole
| Application | Bus
| Technology | AIS
| Monitoring | FALSE
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Drawout Circuit Breakers
Level 1 | SLD Reference | AutoSLDRef_15
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Year of manufacturing | 0
Additional Info | Operation type | Single pole
| Application | Bus
| Monitoring | FALSE
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.001108
| MTTR, hrs | 3.5
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0.69
| MTTM, hrs | 2.06
| Source | IEEE Gold Book, 2007, Table 10.4, pg 233-234
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Clamps
Level 1 | SLD Reference | AutoSLDRef_10
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Year of manufacturing | 0
Additional Info | Operation type | Single pole
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Ground Switches
Level 1 | SLD Reference | AutoSLDRef_16
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Year of manufacturing | 0
Additional Info | Operation type | Single pole
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Disconnect Switches
Level 1 | SLD Reference | AutoSLDRef_17
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
| Type | Disconnect switch
Level 2 | Year of manufacturing | 0
Additional Info | Operation type | Single pole
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.00107
| MTTR, hrs | 3
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0.27
| MTTM, hrs | 2
| Source | IEEE Gold Book, 2007, Table 10.4, pg 249-251
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Combined D_G Switches
Level 1 | SLD Reference | AutoSLDRef_18
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | HV
Level 2 | Type | GIS 1-phase
| Year of manufacturing | 0
Additional Info | Operation type | Single pole
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Fuses
Level 1 | SLD Reference | AutoSLDRef_19
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Year of manufacturing | 0
Additional Info | Rated current, A | 0
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.00137
| MTTR, hrs | 0
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | IEEE Gold Book, 2007, Table 10.4, pg 240-241
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Transformers
Level 1 | SLD Reference | AutoSLDRef_20
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
| Secondary voltage, kV | 0
| Transformer type | Power
| Insulation type | Liquid
Level 2 | Transformer configuration | Three-phase
| Year of manufacturing | 0
Additional Info | Rated power, kVA | 0
| Monitoring | FALSE
| Cooling type | Oil natural – air natural
| Tap changer type | On-load
| Tap changer year | 0
Tap changer manufacturer
Tap changer model
HV bushing manufacturer
HV bushing model
LV bushing manufacturer
LV bushing model
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.0052
| MTTR, hrs | 72
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0.25
| MTTM, hrs | 32
| Source | IEEE Gold Book, 2007, Table 10.4, pg 254-255
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Current Transformers
Level 1 | SLD Reference | AutoSLDRef_21 | AutoSLDRef_4
New SLD Reference
| Bay ID | Default bay | Default bay
| Component technology | AIS | AIS
| Operating voltage, kV | 0 | 40
| Voltage type | MV | HV
Level 2 | Year of manufacturing | 0 | 2000
Additional Info | Type | Current transformer | Current transformer
| Design | Dry | Dry
| Primary rated current, A | 0 | 0
Manufacturer
Model
Serial number
Comments
| Number of secondary cores | 0 | 0
Reliability Data | Library values
| Failure rate, times/yr | 0 | 0
| MTTR, hrs | 0 | 0
| MTTS, hrs | 0 | 0
| Maintenance frequency, times/yr | 0 | 0
| MTTM, hrs | 0 | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0 | 0
| O&M cost, USD/yr | 0 | 0

## Voltage Transformers
Level 1 | SLD Reference | AutoSLDRef_22
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Type | AIS MVT
| Year of manufacturing | 0
Additional Info | Type 2 | Voltage Transformer
| Design | Dry
Manufacturer
Model
Serial number
Comments
| Number of Secondary Cores | 0
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Reactors
Level 1 | SLD Reference | AutoSLDRef_23
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Reactor type | Shunt
| Year of manufacturing | 0
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.10018
| MTTR, hrs | 373
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | Forced Outage Performance of Transmission Equipment for the periods 1/1/1995 to 12/31/1999 (CEA, July 2001), 1/1/2002 to 12/31/2006 (CEA, 2008), 1/1/2005 to 12/31/2009 (CEA, Version 2, April 6, 2011), 1/1/2010 to 12/31/2014 (CEA, October 5, 2015)
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Resistors
Level 1 | SLD Reference | AutoSLDRef_24
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Year of manufacturing | 0
Additional Info | Rated resistance, Ω | 0
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | Forced Outage Performance of Transmission Equipment for the periods 1/1/1995 to 12/31/1999 (CEA, July 2001), 1/1/2002 to 12/31/2006 (CEA, 2008), 1/1/2005 to 12/31/2009 (CEA, Version 2, April 6, 2011), 1/1/2010 to 12/31/2014 (CEA, October 5, 2015)
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Capacitor Banks
Level 1 | SLD Reference | AutoSLDRef_25 | AutoSLDRef_9
New SLD Reference
| Bay ID | Default bay | Default bay
| Component technology | AIS | AIS
| Operating voltage, kV | 0 | 0
| Voltage type | MV | MV
Level 2 | Type | Shunt | Shunt
| Year of manufacturing | 0 | 0
Additional Info | Application | Power factor correction | Power factor correction
Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.17443 | 0.17443
| MTTR, hrs | 2.3 | 2.3
| MTTS, hrs | 2.0415 | 2.0415
| Maintenance frequency, times/yr | 0 | 0
| MTTM, hrs | 0 | 0
| Source | IEEE Gold Book, 2007, Table 10.4, pg 231 | IEEE Gold Book, 2007, Table 10.4, pg 231
User defined values
Failure rate, times/yr
MTTR, hrs
| MTTS, hrs |  | 4
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0 | 0
| O&M cost, USD/yr | 0 | 0

## Surge Arresters
Level 1 | SLD Reference | AutoSLDRef_26 | AutoSLDRef_8
New SLD Reference
| Bay ID | Default bay | Default bay
| Component technology | AIS | AIS
| Operating voltage, kV | 0 | 0
| Voltage type | MV | MV
Level 2 | Year of manufacturing | 0 | 0
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.001317 | 0.001317
| MTTR, hrs | 4 | 4
| MTTS, hrs | 2.0415 | 2.0415
| Maintenance frequency, times/yr | 0 | 0
| MTTM, hrs | 0 | 0
| Source | Forced Outage Performance of Transmission Equipment for the periods 1/1/1995 to 12/31/1999 (CEA, July 2001), 1/1/2002 to 12/31/2006 (CEA, 2008), 1/1/2005 to 12/31/2009 (CEA, Version 2, April 6, 2011), 1/1/2010 to 12/31/2014 (CEA, October 5, 2015) | Forced Outage Performance of Transmission Equipment for the periods 1/1/1995 to 12/31/1999 (CEA, July 2001), 1/1/2002 to 12/31/2006 (CEA, 2008), 1/1/2005 to 12/31/2009 (CEA, Version 2, April 6, 2011), 1/1/2010 to 12/31/2014 (CEA, October 5, 2015)
User defined values
Failure rate, times/yr
| MTTR, hrs |  | 5
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0 | 0
| O&M cost, USD/yr | 0 | 0

## GIS Bushings
Level 1 | SLD Reference | AutoSLDRef_27
New SLD Reference
| Bay ID | Default bay
| Component technology | GIS
| Operating voltage, kV | 0
| Voltage type | HV
Level 2 | Type | SF6/air
| Year of manufacturing | 0
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Loads
Additional Info | SLD Reference | #2
New SLD Reference
| Rated Power | 0
| Maintenance interruption cost | 0
| Maintenance outage duration | 0
| Maintenance outage cost | 0
| Failure interruption cost | 0
| Failure outage duration | 0
| Failure outage cost | 0
Description
Comments

## Motors
Level 1 | SLD Reference | #1
New SLD Reference
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Motor type | Motor generator set
| Motor technology | 3-phase 400 Hz
| Year of manufacturing | 0
Additional Info | Manufacturer
Model
Serial number
| Rated Power | 0
| Maintenance interruption cost | 0
| Maintenance outage duration | 0
| Maintenance outage cost | 0
| Failure interruption cost | 0
| Failure outage duration | 0
| Failure outage cost | 0
Description
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0.00494
| MTTR, hrs | 4
| MTTS, hrs | 2.0415
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
| Source | IEEE Gold Book, 2007, Table 10.4, pg 242
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0

## Protection relays
Level 1 | SLD Reference | AutoSLDRef_14
New SLD Reference
| Bay ID | Default bay
| Component technology | AIS
| Operating voltage, kV | 0
| Voltage type | MV
Level 2 | Type | Electromechanical
| Year of manufacturing | 2004
Additional Info | Manufacturer
Model
Serial number
Comments
Reliability Data | Library values
| Failure rate, times/yr | 0
| MTTR, hrs | 0
| MTTS, hrs | 0
| Maintenance frequency, times/yr | 0
| MTTM, hrs | 0
Source
User defined values
Failure rate, times/yr
MTTR, hrs
MTTS, hrs
Maintenance frequency, times/yr
MTTM, hrs
Source
Other | Capital cost, USD | 0
| O&M cost, USD/yr | 0